## Slide 1: NetApp FAS6220 cDOT Shared Standard Architecture
Mike Arndt, Systems Engineer
2013-10-23

## Slide 2: Overview
Clustered Data ONTAP (cDOT) 8.2
  Non-disruptive operations and QOS enabled by CDOT
  8.2.1GA expected in January 2014 and recommended for shared systems
Primary storage cluster design
  A mix of high tier and low tier HA pairs in each cluster
    8 node maximum (4 HA pairs) to support QOS
  FlashPool based design for High Tier
    The mix of SSD and 600GB 10k SAS drives mitigate performance impact of the industry moving away from 15k drives
  SATA with FlashCache design for Low Tier
    Keep cost down for applications without high performance requirements by using 2TB SATA drives
SnapVault secondary system design
  Single node system
  DS4486 disk shelves with 4TB drives provide low cost and high density for backup systems

## Slide 3: High Tier
High Tier Standard Architecture:
  FAS6220 HA Pair
  DS2246 shelves of 600GB 10k SAS drives
    6 shelves in base configuration
    12 shelves in maximum configuration
  DS2246 shelves of 200GB SSD drives
    2 shelves of 12 drives
    1500GB of cache per controller
  10GbE connectivity for data access
  1GbE connectivity for management
  Software licenses:
    NFS and CIFS protocols
    SnapMirror, SnapVault, and SnapRestore

## Slide 4: High Tier: Performance Scaling
Base configuration of 3 shelves per controller:
  27TB usable per controller
Maximum configuration of 6 shelves per controller:
  56TB usable per controller
Peak throughput at 32k 50/50 read/write mix:
  1054MB/sec per controller
    33,750 IOPs per controller
Peak IOPs at 4k 50/50 read/write mix:
  53,000 IOPs per controller
    207MB/sec per controller
Performance profile limits:
    18.8MB/sec per TB
    946 IOPs per TB
    These values assume possible performance degradation during a cluster failover event

## Slide 5: Low Tier
Low Tier Standard Architecture:
  FAS6220 HA Pair
  DS4246 shelves of 2TB 7.2K SATA drives
    4 shelves in base configuration
    6 shelves in maximum configuration
  512GB of FlashCache per controller
  10GbE connectivity for data access
  1GbE connectivity for management
  Software licenses:
    NFS and CIFS protocols
    SnapMirror, SnapVault, and SnapRestore

## Slide 6: Low Tier: Performance and Capacity Scaling
Base config of 2 shelves per controller:
  52TB usable per controller
Maximum config of 3 shelves per controller:
  78TB usable per controller
Peak throughput at 32k 50/50 read/write mix:
  687MB/sec per controller
    22,000 IOPs per controller
Peak IOPs at 4k 50/50 read/write mix:
  36,000 IOPs per controller
    140MB/sec per controller
Performance profile limits:
    8.6MB/sec per TB
    461 IOPs per TB
    These values assume possible performance degradation during a cluster failover event

## Slide 7: SnapVault Secondary
SnapVault Secondary Standard Architecture:
  FAS6220 single node cDOT system
    Single node systems are preferred to accommodate cluster peer limitation of 8 peers per cluster
  DS4486 shelves of 4TB 7.2K SATA drives
    1 shelves in base configuration
    4 shelves in maximum configuration
      Based on estimations of hitting 1000 volume limit
  10GbE connectivity for data access
  1GbE connectivity for management
  Software licenses:
    NFS and CIFS protocols
    FlexClone, SnapMirror, SnapVault, and SnapRestore

## Slide 8: Cluster Network
FAS6220 shared primary storage configured as switched clusters at initial installation
NetApp CN1610 cluster network switches
  Low cost NetApp branded switch
  No customer setup required, complete config available from support.netapp.com
  Supports up to 8 node clusters
SnapVault secondary will be configured as single node systems
  8 cluster peers are supported per cluster, so configuring single node backup systems helps avoid hitting the cluster peer limit

## Slide 9: Requirements / Limitations in cDOT 8.2.1
1000 volumes per controller
125 Vservers per controller
125 LIFs per controller
10M maximum distance from controllers to all disk shelves
5M distance from controllers to private cluster switches with copper cabling
300M distance from controllers to private cluster switches with optical cabling
8 cluster peers

## Slide 10: FAS/V6200 Controller I/O Standalone Controller
10GbE
e0a, e0b
Management
ACP
USB
(disabled)
e0M / SP
GbE
e0c, e0d, e0e, e0f
Vertical I/O
Slot 1
PCIe v2.0
Slots
Slots 3,4,5,6
8Gb FC
0a, 0b, 0c, 0d
Serial
Console
10/100 Ethernet
NVRAM8
(Slot 2)
A single stack will be used for

## Slide 11: High Tier Controller Configuration Details

## Slide 12: Low Tier Controller Configuration Details

## Slide 13: Backup Controller Configuration Details

## Slide 14: HA Pair SAS Connectivity
Cable shelf to shelf IOMs from OUT ● to IN ■
First stack shelf IDs start with 00 and count up
Second stack shelf IDs start with 10 and count up

## Slide 15: Single Controller SAS Connectivity
Cable shelf to shelf IOMs from OUT ● to IN ■
First stack shelf IDs start with 00 and count up
Second stack shelf IDs start with 10 and count up

## Slide 16: HA Pair ACP Connectivity
Cable shelf to shelf ACPs from OUT ● to IN ■
Use locked wrench port on FAS6220 for ACP connections

## Slide 17: Single Controller ACP Connectivity
Cable shelf to shelf ACPs from OUT ● to IN ■
Use locked wrench port on FAS6220 for ACP connections

## Slide 18: Disk Shelf Connectivity Details
High Tier systems with FlashPool will use a dedicated stack for the shelf of SSD drives on each controller and a dedicated stack for the shelves of SAS drives on each controller
    Ports 1a/3b will connect to HT A SSD shelf (00)
    Ports 3a/1d will connect to HT B SSD shelf (10)
    Ports 1c/3d will connect to HT A SAS shelves (2x)
    Ports 3c/1b will connect to HT B SAS shelves (3x)
    Ports 1a/3a/1c/3c connect to square shelf ports
    Ports 1b/3b/1d/3d connect to circle shelf ports
Low Tier and Backup systems will use a single stack on each controller.

## Slide 19: Network Connectivity Details
The SP is the wrench port on the FAS6220
The locked wrench port on the FAS6220 is used for ACP connectivity to the shelves
The e0a 1GbE port is used for management network connectivity
  This should be a 1GbE connection, not 100Mb
The e0c and e0e ports are used for the private cluster network
The e0d and e0f 10GbE ports should be used to create a LACP ifgrp for data access
Additional NICs are required for connectivity to a different physical data network

## Slide 20: FAS6220 Primary – Initial Cabinet Layout

## Slide 21: FAS6220 Primary – Final Cabinet Layout

## Slide 22: FAS6220 Backup – Initial Cabinet Layout

## Slide 23: FAS6220 Backup - Final Cabinet Layout

## Slide 24: High Tier Aggregate Sizing and Growth
ONTAP VERSION | Clustered ONTAP 8.2.1 or higher
LIMITATIONS | Maximum aggregate size of 324TB Maximum volume size of 70TB
AGGREGATE CONFIGURATION | Dedicated 3 disk root aggregate on each node is required One FlashPool data aggregate per node.
RAID GROUP SIZE | 11 SSD drives in their own raid group of the FlashPool aggregate 19 SAS drives per raid group in the FlashPool aggregate Note: aggregates should be grown in 9, 10, or 19 drive increments
INITIAL CONFIGURATION 6 DS2246 shelves | 1 root aggregate with 3 SAS drives per controller 1 data aggregate of 1 SSD raid group (11 drives) and 3.5 SAS raid groups (67 drives) per controller 2 spare drives per controller 27TB usable per controller = 54TB total
FINAL CONFIGURATION 12 DS2246 shelves | 1 root aggregate with 3 SAS drives per controller 1 data aggregate of 1 SSD raid group (11 drives) and 7 SAS raid groups (133 drives) per controller 8 spare drives per controller 56TB usable per controller = 112TB total

## Slide 25: Low Tier Aggregate Sizing and Growth
ONTAP VERSION | Clustered ONTAP 8.2.1 or higher
LIMITATIONS | Maximum aggregate size of 324TB Maximum volume size of 70TB
AGGREGATE CONFIGURATION | Dedicated 3 disk root aggregate on each node is required One data aggregate per node.
RAID GROUP SIZE | 14 SATA drives per raid group in the data aggregate Note: aggregates should be grown in 8 or 14 drive increments
INITIAL CONFIGURATION 4 DS4246 shelves | 1 root aggregate with 3 SATA drives per controller 1 data aggregate of 3 raid groups (42 drives) per controller 3 spare drives per controller 52TB usable per controller = 104TB total
FINAL CONFIGURATION 6 DS4246 shelves | 1 root aggregate with 3 SATA drives per controller 1 data aggregate of 4.5 raid groups (64 drives) per controller 5 spare drives per controller 78TB usable per controller = 156TB total

## Slide 26: Backup Aggregate Sizing and Growth
ONTAP VERSION | Clustered ONTAP 8.2.1 or higher
LIMITATIONS | Maximum aggregate size of 324TB Maximum volume size of 70TB 4 spare drives per node recommended for DS4486 shelves 8 cluster peers
AGGREGATE CONFIGURATION | Dedicated 3 disk root aggregate on each node is required 2 data aggregates per node.
RAID GROUP SIZE | 16 SATA drives per raid group in the data aggregate Note: aggregates should be grown in 9 or 16 drive increments
INITIAL CONFIGURATION 1 DS4486 shelf | 1 root aggregate with 3 SATA drives 1 data aggregate of 2.5 raid groups (41 drives) 4 spare drives per controller 114TB usable
FINAL CONFIGURATION 4 DS4486 shelves | 1 root aggregate with 3 SATA drives 1 data aggregates of 5.5 raid groups (89 drives) 1 data aggregates of 6 raid groups (96 drives) 4 spare drives per controller 523TB usable